SECTION 08 71 13 – AUTOMATIC DOOR OPERATORS

GENERAL

- <SPECIFIER:  Edit this specification as required for the project>

SUMMARY

Furnish and install the following types of automatic door operators:

Low energy automatic door operators for swinging doors.

Power assist door operators for swinging doors.

REFERENCES

UNDERWRITERS LABORATORIES (UL):

UL 325 – Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

UL10C – Standard for Positive Pressure Fire Tests of Door Assemblies.

American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA):

ANSI/BHMA A156.19 Standard for Power Assist and Low Energy Power Operated Swinging Doors.

American Society for Testing and Materials (ASTM):

ASTM B221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

American Association of Automatic Door Manufacturers (AAADM).

National Fire Protection Association (NFPA):

NFPA 101 – Life Safety Code.

NFPA 80 – Standard for Fire Doors and Other Opening Protectives.

NFPA 70 – National Electrical Code.

International Code Council (ICC):

[IBC:  International Building Code.]

[CBC: California Building Code.]

National Association of Architectural Metal Manufacturers (NAAMM):

Metal Finishes Manual for Architectural and Metal Products.

American Architectural Manufacturers Association (AAMA):

AAMA 607.1 - Clear Anodic Finishes for Architectural Aluminum.

PERFORMANCE REQUIREMENTS

Temperature Change:

Operator capable of operating within temperature ranges of -40°F and 140°F (-40 C to 60 C).

SUBMITTALS

Product Data: Provide complete product and installation documentation as provided by the manufacturer.

Shop Drawings: Provide shop drawings for automatic door operators including elevations, sections, and details of construction.  Include profiles, dimensioned layout, motion /presence sensor control devices, finish, electrical, and anchoring requirements.

Informational Submittal:  Manufacturer's product information indicating the  available sustainability credits that can contribute towards LEED certification.

Manufacturer's certificate indicating percentage of pre-consumer, post-consumer, and new content in the extruded aluminum.

Samples: Submit manufacturer’s finish samples.

Provide manufacturer’s operating and maintenance manual.  The manual to include the name, address, and contact information of the manufacturer providing the operators and their nearest service representatives.  A spare parts list shall also be included.

Provide manufacturer’s warranty documentation.

QUALITY ASSURANCE

Manufacturer must have a minimum of ten (10) years experience in the fabrication of equipment similar to those specified.

Automatic door operators shall be obtained solely through an authorized trained and factory certified provider.

Obtain automatic door operators and installation services through one source from a single manufacturer.

Automatic door operators shall be certified to meet performance design criteria of the following standards.

ANSI/BHMA 156.19

NFPA 101

UL 325

UL Listed fire door operator with automatic closure.

IBC

Installation shall be approved by an AAADM certified inspector.

COORDINATION

Coordinate door operators with doors, frames, door hardware, and related work to ensure proper size, thickness, hand, function and finish.

Coordinate power requirements, layout, and connections to power supplies with installation of automatic door operators.

WARRANTY

Project Warranty:  Automatic door operators shall be warranted against defect in material and workmanship for a period of two years from the date of manufacturer shipment.

During the warranty period a factory-trained technician shall perform service and repairs. An inspection shall be performed after each adjustment or repair.

During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.

PRODUCT

MANUFACTURER

- Record-USA

- Monroe, North Carolina, USA

- (800) 438-1937

MATERIALS

Aluminum:  Alloy and temper recommended by manufacturer as indicated below:

Aluminum Extrusions:  Alloy 6063-T5.

AUTOMATIC DOOR OPERATORS

Low energy automatic door operators shall be furnished with all required components for a complete installation.  Automatic door operators shall include the following:

Automatic door operator

Operator housing

Connecting hardware

Activation and safety devices

Basis of Design:  Record 8100 low energy automatic door operator:

Applicable Standard:  ANSI/BHMA A156.19.

Operator:  Non-handed, electro-mechanical operator, powered by 24 volt, 1/4 hp pulse-modulated motor.

Automatic door operator shall be able to operate and control a door leaf weighing up to 1200 pounds (544.3 kg).  Consult factory when door exceeds 350 pounds (158.8 kg).

The pulse-modulated motor cycles on/off quickly during use resulting in an energy efficient motor that operates with minimal wear and negligible heat.

Configuration:  Operator to control single or pairs of swinging doors as indicated on the drawings and specified below:

Traffic Pattern:  [One way.]  [Two way.]  [Double egress.]

[Pairs of Doors:  [Simultaneous swing.]  [Single leaf operation.]

[Double Egress Doors:  [Simultaneous swing.]  [Independent operation.]

Operator Housing:  The extruded aluminum operator housing, 5” wide x 4-1/2” high (127 mm x 114 mm). The Length of the operator housing determined by site conditions and/or specifications herein.

Length of Housing:  Continuous full width of door, unless indicated otherwise.

Structural walls of the base plate have a minimum thickness of 0.187” (3/16”), housing wall thickness of 0.09” (3/32”).

[An access port on the bottom of the housing eliminates the need to remove the cover for service or adjustment.]

Connecting Hardware: Surface mounted operator is connected to the top face of the swing door by means of an aluminum / steel arm.

The arm shall allow opening angles to 130 degrees.

The arm is equipped with a mechanical device which will sheer in the case of extreme force or wind.

Electronic Controls: Microprocessor controlled unit shall control the operation and switching of the swing operator. The microprocessor control to provide low voltage power supply for all means of actuation.  The controls include time delay for normal cycle.

Control will accept signals from peripheral devices such as motion and safety sensors.

[On board system monitoring with 24/7 feedback when equipped with the S.M.A.R.T. Panel LCD Display. The unit will display the status of the operator, any faults that occurred and contact information for fault notification.]

Microprocessor shall be easily updated with new software versions.

Control Switch: A three position switch mounted in the end cover of the housing along with a “fault warning” LED. The switch is marked On/Off/Hold Open.

The LED will flash if the microprocessor detects a fault.

Door Operation:

Power Open: When an opening signal is received, the door will open at the pre-set operator opening speed. At back check, the door slows, and at the pre-selected opening angle the door stops.

If the door is obstructed while opening, it will either stop or reverse (field selectable).

The open position is held by the motor.

Opening Angle: The operator shall have a field adjustable opening angle from 80 degrees to 180 degrees as follows:

Standard arm push side - opening angle to 130 degrees.

Standard arm pull side - opening angle to 98 degrees.

Track arm pull side - opening angle to 180 degrees.

Track arm push side - opening angle to 98 degrees.

Spring Close: An adjustable tension spring shall provide closing.

When the hold open time has elapsed, the operator will close the door automatically, using the motor and spring force. The door will slow at latch check.

The door is kept closed by spring power or extended closing force by the motor.

Power Assist: Operator can be adjusted to provide a lower opening force while pushing or pulling the door manually.  Operator allows the door to close when an opening force is no longer applied to the door.

Power assist force is field adjustable from 5 lbf to 15 lbf maximum.

Electronic Dampening:  The operator automatically counteracts additional forces applied to the door during the opening or closing cycle by reducing the door speed.

Stack Pressure Control: The opening force is electronically controlled to overcome changes of stack pressure.  This control automatically compensates for manual push force.

Lock Engage Circuit: If latching of the door is unsuccessful when at the closed position, the operator will automatically reopen door to 10 degrees and retry closing in an attempt to successfully latch the door.

Door Coordinator: Door movement for a pair of doors with an astragal is sequenced to allow for coordinated opening and closing of doors.

Monitored Safety Sensors: Safety sensors are monitored, and automatic door activation is prevented if a sensor failure occurs.  The door will function as a manual swing door and a fault is registered in the controls log.

Fire-Rated Doors:  Automatic door operator listed and labeled by a qualified testing agency for use on fire-rated door assemblies that comply with NFPA 80.

- <SPECIFIER:  Two 18 gauge low voltage stranded wires are required from the automatic door operator to each activation device (wire length 50 feet maximum)>

Electrical Characteristics: Nominal power consumption is 67 watts, 0.08 amps at 120 VAC. Peak power consumption is 2.9 amps and standby power consumption is 0.02 amps.

Overload Protection: Motor is equipped with built-in thermal overload protection.

[Battery Back-up: Header mounted battery provides power for continues operation during power failure. Battery has a warning signal if not working properly.

Battery shall be capable of full operation including powered locking for approximately 200 cycles.]

Cycle Counter:  Operator has integrated digital cycle counter that includes total operation time.

SIGNAGE: Provide signage in accordance with ANSI/BHMA A156.19.

ACTIVATION AND SAFETY DEVICES

General:  Provide activation and safety devices in accordance with ANSI/BHMA standards, for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate activation and safety devices with door operation and door operator mechanisms.

[Knowing Act Activation Device:]

- <SPECIFIER:  Select types of activation device(s) as required for project.>

[Push Plate:  [Flush mounted,]  [Surface mounted,] hard wired,  [4-1/2 inch square]  [6 inch round] stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

[Jamb Mounted Push Plate:  Hard wired, 1-1/2 inch x 4-3/4 inch, stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

[Radio Controlled Push Plate:  [Flush mounted,]  [Surface mounted,]  [4-1/2 inch square]  [6 inch round] stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

[Touchless Sensor Plate:  [Flush mounted,]  [Surface mounted,] hard wired,  [2-3/4 inch x 4-1/2 inch]  [4-1/2 inch square]  [black polycarbonate]  [stainless steel] sensor plate switches engraved with "Push to Open" and a handicap logo. Microwave technology with an adjustable activation range.]

- <SPECIFIER:  Door can be used manually with no damage to the operator.>

[Push Activation:]

Pushing or pulling the door open from any position shall activate the opening cycle of the operator. Operator will power the door open and after the hold open time has elapsed, the door will close.  This is a programmable feature of the operator.

[Power Assist Activation:]

Operator provides a lower opening force while pushing or pulling the door manually.  Operator allows the door to close when an opening force is no longer applied to the door.

- <SPECIFIER:  Contact Record for safety device recommendations – safety sensors are not required by ANSI/BHMA A156.19 for low energy operators>

- Suggested use of safety sensors for low energy operators include door openings subject to elderly or patient use, door openings with gurney or equipment traffic, door openings where people constantly piggy-back through the door, etc.

- <SPECIFIER:  Retain the following if safety devices are required for the project>

[Safety Devices:]

Door Mounted Presence Sensors: Infrared presence safety device (mounted at top of each door); adjusted to provide detection field sizes as recommended by ANSI/BHMA A156.10.

Unit to provide detection during the travel of the door.

Upon detection the sensor shall provide a signal to stop or reverse the door action.

- <Specifier: Select one of the following mounting options for door mounted safety devices>

[The door mounted safety sensor devices shall be mounted on both the swing (pull) side and the approach (push) side of the door (2 safety sensors per leaf), providing detection on both sides of the door.]

[The door mounted safety sensor devices shall be mounted on the swing (pull) side of the door (1 safety sensor per leaf), providing detection on one side of the door only.]

[The door mounted safety sensor devices shall be mounted on the approach (push) side of the door (1 safety sensor per leaf), providing detection on one side of the door only.]

ALUMINUM FINISHES

Comply with NAAMM’s “Metal Finishes Manual for Architectural and Metal Products” for applying and designing finishes. Finish designations beginning with “AA” comply with requirements established by American Architectural Manufacturers Association (AAMA).

- <SPECIFIER:  Select finish as required for project>

[Clear Anodized:  Architectural Class I Anodized Coating (AA-M12C22A41).]

[Dark Bronze Anodized:  Architectural Class I Anodized Coating (AA-M12C22A44).]

[Medium Bronze Anodized:  Architectural Class I Anodized Coating (AA-M12C22A44).]

[Light Bronze Anodized:  Architectural Class I Anodized Coating (AA-M12C22A44).]

[Champagne Anodized:  Architectural Class I Anodized Coating (AA-M12C22A44).]

[Black Anodized:  Architectural Class I Anodized Coating (AA-M12C22A44).]

[Kynar Paint Coating:  As selected by Architect from full range of industry colors and color densities.]

[Powder Coat:  To match Architect’s sample.]

[Stainless Steel Clad:  [Polished, non-directional finish.]  [Satin finish.]

[Brass Clad:  [Polished, non-directional finish.]  [Satin finish.]

EXECUTION

INSPECTION

Examine conditions for compliance with requirements for installation tolerances, door and frame preparation, reinforcements, and other conditions affecting performance of automatic door operators.

Examine roughing-in for electrical source power to verify actual locations of wiring connections.

Provide written notification to the appropriate personnel of conditions not acceptable to the installer and/or manufacturer. Proceed with installation only after necessary corrections are made to insure a suitable opening.

INSTALLATION

General:  Install automatic door operators according to manufacturer's written instructions and ANSI/BHMA A156.19 standard, including signage, controls, wiring, and connection to the building's power supply.

Do not install damaged components.  Fit joints to produce hairline joints free of burrs and distortion.

Install operators true in alignment with established lines and door geometry without warp or rack.  Anchor securely in place using specified fasteners, as required by installation instructions, and as detailed on the shop drawings.

Install surface-mounted hardware using concealed fasteners to greatest extent possible.

Door Operators:  Connect door operators to electrical power distribution system as specified in Division 26 Sections.

Activation and Safety Devices:  Install devices and wiring according to manufacturer's written instructions, cited ANSI/BHMA standard for type of operator and direction of pedestrian travel, and as specified Division 26 Sections.

Access-Control Devices:  Connect access-control devices to access-control system as specified in Division 28 Sections.

Signage:  Apply on both sides of each door as required by ANSI/BHMA standards for the type of door operator and direction of pedestrian travel.

ADJUSTING

Adjust automatic door operators to function smoothly and lubricate as recommended by manufacturer; comply with requirements of applicable ANSI/BHMA standards.

Adjust operators on exterior doors for weathertight closure.

FIELD QUALITY CONTROL

An AAADM certified technician shall inspect and approve automatic door operators for compliance with the ANSI/BHMA. The certified technician shall be approved by the manufacturer.

CLEANING

Clean metal surfaces promptly after installation.  Remove excess sealant, dirt, and other substances.  Repair damaged finish to match original finish.

Clean adjacent surfaces soiled by door operator installation.

DEMONSTRATION

Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain automatic door operators.

- END OF SECTION 08 71 13