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SECTION 08 71 13 – AUTOMATIC DOOR OPERATORS
GENERAL
SUMMARY
<SPECIFIER: Edit this specification as required for the project>
<SPECIFIER: This specification is for automatic door operators complying with ANSI/BHMA A156.19 for low energy door applications.>
This section includes the following types of automatic door operators:
Low energy door operators for swinging doors.
Related Sections:
Division 26 and 28 Sections for electrical connections including conduit and wiring for automatic entrance door operators and access control devices.
REFERENCES
References:  Refer to the version year adopted by the Authority Having Jurisdiction.   
ANSI A117.1 - Accessible and Usable Buildings and Facilities.
ICC/IBC - International Building Code.
CUL – Approved for use in Canada.
NFPA 70 - National Electrical Code.
NFPA 80 - Fire Doors and Windows.
NFPA 101 - Life Safety Code.
NFPA 105 - Installation of Smoke Door Assemblies.
American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA).
[ANSI/BHMA A156.10 American National Standard for Power Operated Pedestrian Doors.]
ANSI/BHMA A156.19 Standards for Power Assist and Low Energy Power Operated Doors.
Underwriters Laboratories (UL). 
UL 10 (b) Standard for Safety – Fire Tests of Door Assemblies
UL 10 (c) Standard for Positive Pressure Fire Tests of Door Assemblies
UL 325 Standard for Safety for Door, Drapery, Gate, Louver and Window Operators and Systems.
Canadian Standards Association (CSA)
American Association of Automatic Door Manufacturers (AAADM).
American Society for Testing and Materials (ASTM).
ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.
ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.
American Architectural Manufacturers Association (AAMA).
AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.
National Association of Architectural Metal Manufacturers (NAAMM).
Metal Finishes Manual for Architectural Metal Products.
International Code Council (ICC).
[IBC:  International Building Code.]
[CBC: California Building Code.]
DEFINITIONS
Activation Device: Device that, when actuated, sends an electrical signal to the door operator to activate the operation of the door.
Knowing act:	Consciously initiating the opening of a power operated door using acceptable methods including wall mounted switches such as push plates and controlled access devices such as keypads, card readers and key switches.
Double Egress Doors:  A pair of doors that swing with the two doors moving in opposite directions and no mullion between them.
PERFORMANCE REQUIREMENTS
Automatic door equipment accommodates medium pedestrian traffic.
Opening Force Requirements:  Doors shall open with a manual force, not to exceed 30lbf (133N) to set the door in motion and 15 lbf to fully open the door applied at 1” (25 mm) from the latch edge of the door.  The force required to prevent a stopped door from opening or closing shall not exceed 15 lbf (67 N) measured 1” (25 mm) from the latch edge of the door at any point during opening or closing.  
Closing Time:
Doors shall be field adjustable to close from 90 degrees to 10 degrees in 3 seconds or longer as applicable per ANSI/BHMA A156.19 standards.
Doors shall be field adjusted to close from 10 degrees to fully closed in not less than 1.5 seconds.
SUBMITTALS
Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.
Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, operator, motion /presence sensor control device, anchors, hardware, finish, options and accessories.
Indicate required clearances, and location and size of each field connection.
Indicate locations and elevations of entrances showing activation and safety devices.
Wiring Diagrams:  For power, signal, and activation / safety device wiring.
Samples: Submit manufacturer’s samples of aluminum finish.
Manufacturers Field Reports:  Submit manufacturer’s field reports from AAADM certified technician of inspection and approval of doors for compliance with ANSI/BHMA after completion of installation.
Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the work of this section in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the operators and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.
Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.
QUALITY ASSURANCE
Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.  Manufacturer to have a company certificate issued by AAADM.
Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum 3 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.
Certified Inspector Qualifications: Certified by AAADM.
Source Limitations for Automatic Door Operators:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.
Certifications: Operators shall be certified by the manufacturer to meet performance design criteria in accordance with the following standards.
ANSI/BHMA A156.19 American National Standard for Power Assist and Low Energy Operated Doors.
NFPA 101 - Life Safety Code.
UL 325 - Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.
UL 10 (b) Standard for Safety – Fire Tests of Door Assemblies
UL 10 (c) Standard for Positive Pressure Fire Tests of Door Assemblies
CAN/CSA C22.2 NO 247 Operators and systems of doors, gates, draperies, and louvres
CAN/ULC S104 Standard Method for Fire Tests of Door Assemblies
Emergency Exit Door Requirements: Comply with requirements of authorities having jurisdiction for automatic entrance doors serving as a required means of egress.
COORDINATION
Coordinate door operators with doors, frames and related work to ensure proper size, thickness, hand, function and finish. Coordinate hardware for automatic entrances with hardware required for rest of the project.
Electrical System Roughing-in: Coordinate layout and installation of power door operators with connections to power supplies and access control system as applicable.
WARRANTY
General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.
Automatic Door Operators shall be free of defects in material and workmanship for a period of two years from the date of manufacturer shipment.
During the warranty period a factory-trained technician shall perform service and affect repairs. An inspection shall be performed after each adjustment or repair. 
During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.
PRODUCTS
MANUFACTURER
Record-USA
4324 Phil Hargett Court
Monroe, North Carolina, USA
(800) 438-1937
<SPECIFIER: Revise the following substitution clause as required by project requirements.  Select either Item “B” or “C”>
[Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]  
[Substitutions:  Not Permitted.]  
MATERIALS
Aluminum:  Alloy and temper recommended by manufacturer for type of use and finish indicated, as indicated below:
Extruded Aluminum, Alloy 6063-T5.
SWING DOOR OPERATORS
0. Model:  Record HA8 low energy automatic door operator (Basis of Design):  
<SPECIFIER: Select the following options as required for the project>
Reference Standard:  ANSI/BHMA A156.19.
Configuration:  Operator to control single swinging doors and pairs of swinging doors as indicated on the drawings and specified below:
Traffic Pattern:  [One way.]  [Two way.]
[Pairs of Doors:  [Simultaneous swing.]  [Single leaf operation.]
[Double Egress Doors:  [Simultaneous swing.]  [Independent operation.]
Automatic Door Operator:  Electro-mechanical, non-handed operator, powered by 24 volt, 1/8 hp motor.  Spring shall be adjustable to compensate for different manual push forces required on varying door widths.
Automatic operator shall be capable of operating and controlling up to a 250 pounds (113 kg) door, 48 inches (1219 mm) in width.
Surface Mounted Operator:
Side Access Operator Housing:  Operator is contained in 4-3/4” (121 mm) deep x 5” (127 mm) high extruded aluminum housing with a removable cover.
Surface Mounted Housing:  [Standard Width.]  [Continuous for full width of door.] 
Connecting Hardware: Surface mounted operators to have a steel arm from the operator, mounted to the top face of the swing door. 
Operator Temperature Range:  Capable of operating within temperature ranges of -4F (-20C) and 120F (50C).
Door Operation:  
Opening Cycle:  The adjustable speed operator shall control the door opening to the back check position, where the opening speed is reduced.
Manual door operation with operational forces of 15 lbs maximum to fully open the door applied at 1” (25 mm) from the latch edge of the door.
Hold Open:  The operator shall stop and hold the door open at the selected door opening angle for an adjustable period of time.
Closing Cycle:  Operator shall close door by spring energy, employing the motor as a dynamic brake to control closing speed.  Closing spring shall be pre-loaded for positive closing action at low material stress level.
Obstruction Control:  The operator will stop and reverse the door movement during opening cycle.
Electronic Controls:  Microprocessor controlled unit shall control the operation and switching of the swing power operator.  The microprocessor unit provides low voltage power supply for all means of actuation.
Control Switch: Automatic door operators shall be equipped with the following type of multi-position function switch: 
3 position rocker switch mounted on end cap (On-Off-Hold).

<SPECIFIER: Select the additional power supply if more power is needed.>

Electric Strike Integration:  Onboard 250 mA 24VDC power supply.
[Provide additional 1.1A 24VDC power supply.]
ACTIVATION DEVICES  
<SPECIFIER: Select the type of activation devices and safety devices required for the project>
General:  Provide activation devices in accordance with ANSI/BHMA standards, for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate activation and safety devices with door operation and door operator mechanisms.
<SPECIFIER: Select the type of knowing act activation devices if required for the project>
[Knowing Act Activation Device:]   
[Push Plate:  Hard wired, [4-1/2 inch square]  [6 inch round] stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]
[Push Plate:  Jamb mounted, hard wired, 1-1/2 inch x 4-3/4 inch, stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]
[Push Plate:  Radio controlled, wireless, [4-1/2 inch square]  [6 inch round]   stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]
[Sensor Plate:  Touchless, [2-3/4 inch x 4-1/2 inch]  [4-1/2 inch square] activation senor plates, black polycarbonate with white letters.  Microwave technology has an adjustable range of 2 inches to 24 inches.]
<SPECIFIER: Consult Record for safety device recommendations – safety sensors are not required by ANSI/BHMA A156.19 for low-energy operators>
<SPECIFIER: Retain the following if safety devices are required for the project – requires “safety sensor integration” option on power operator>
[SAFETY DEVICES]  
General:  Provide safety devices in accordance with ANSI/BHMA A156.10 standards, for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate safety devices with door operation and door operator mechanisms.
Safety Devices:
Door Mounted Presence Sensor:  Shall be a door mounted infrared presence safety device (mounted at top of each door); adjustable to provide detection field sizes and functions required by ANSI/BHMA A156.10.
Unit to provide detection during the travel of the door.
Upon detection the sensor shall provide a signal to stop or reverse the door action. 
Door Mounted Safety Sensor Devices:  Safety sensor devices shall be door mounted as specified.
<SPECIFIER: Select one of the following mounting options for door mounted safety sensor devices>
[The door mounted safety sensor devices shall be mounted on both the swing (pull) side and the approach (push) side of the door (2 safety sensors per leaf), providing detection on both sides of the door.] 
[The door mounted safety sensor devices shall be mounted on the swing (pull) side of the door (1 safety sensor per leaf), providing detection on one side of the door only.]
[The door mounted safety sensor devices shall be mounted on the approach (push) side of the door (1 safety sensor per leaf), providing detection on one side of the door only.]
<SPECIFIER: Coordinate with the Architect if an EPT (electrical power transfer) is required in lieu of the standard door cord power transfer – EPT specified in Division 8 Section “Door Hardware”>
Power transfer from the door mounted safety sensor to operator shall be [through an exposed door cord]   [through an EPT (electrical power transfer) specified in Division 8 Section “Door Hardware”.]
ALUMINUM FINISHES   
<SPECIFIER: Consult Record for custom finish options>
Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.
Automatic Door Operator Enclosure:
[Anodized Finish:]
[AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]  
[AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]
[AAMA 611, Black, AA-M12C22A44, Class I, 0.018 mm.]
EXECUTION
EXAMINATION
Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance of swinging power operated doors.
Examine roughing-in for electrical source power to verify actual locations of wiring connections.
Proceed only after such discrepancies or conflicts have been resolved.
INSTALLATION
Do not install damaged components.  Fit joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.
Operators:  Install automatic door operators plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.
Install surface mounted hardware using concealed fasteners to greatest extent possible.
Set headers, carrier assemblies, tracks, operating brackets and guides level and true to location with anchorage for permanent support.
Door Operators:  Connect door operators to electrical power distribution system [and fire detection system] as specified in Division 26 Sections.
Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to seal between the operator housing and the adjacent surfaces.
Signage:  Apply signage on both sides of each door and sidelite as required by ANSI/BHMA A156.19 and manufacturers installation instructions.
ADJUSTING
Adjust automatic door operators, controls and hardware for smooth and safe operation and for weather tight closure. Adjust doors in compliance with ANSI/BHMA A156.19.
FIELD QUALITY CONTROL
Before placing doors into operation, AAADM certified technician shall inspect and approve doors for compliance with ANSI/BHMA A156.19.  Certified technician shall be approved by manufacturer.
CLEANING AND PROTECTION
Clean adjacent surfaces soiled by automatic door operator installation.
Clean metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages and finish to match original finish.
DEMONSTRATION
Engage a factory-authorized representative to train Owner's maintenance personnel to adjust, operate, and maintain safe operation of the door.
END OF SECTION
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