SECTION 08 42 43 – INTENSIVE CARE UNIT/CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

GENERAL

SUMMARY

- NOTE:  Edit this specification as required for the project

This section includes the following types of intensive care unit/critical care unit (ICU/CCU) entrance doors:

Manually operated sliding ICU/CCU entrances.

Related Sections:

Division 7 Sections for caulking to the extent not specified in this section.

Division 8 Section “Glazing” for materials and installation requirements of glazing for ICU/CCU entrance doors.

- NOTE:  Delete the following if magnetic hold-open devices are not required

[Division 26 and 28 Sections for connections to smoke/fire detection systems.]

REFERENCES

References:  Refer to the version year adopted by the Authority Having Jurisdiction.

ANSI A117.1 - Accessible and Usable Buildings and Facilities.

ICC/IBC - International Building Code.

NFPA 101 - Life Safety Code.

American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA).

ANSI Z97.1 Standards for Safety Glazing Material Used in Buildings.

American Society for Testing and Materials (ASTM).

ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.

ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.

American Architectural Manufacturers Association (AAMA).

AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

National Association of Architectural Metal Manufacturers (NAAMM).

Metal Finishes Manual for Architectural Metal Products.

International Code Council (ICC).

[IBC:  International Building Code Building Code.]

[CBC: California Building Code.]

PERFORMANCE REQUIREMENTS

- NOTE:  Delete the following if MicroShield is not required

[MicroShieldTM antimicrobial silver-based ion finish on all exposed surfaces including door pulls, door extrusions, rails and header to comply with the manufacturer’s specified requirements.]

Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew.

SUBMITTALS

Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.

Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, and fabrication of doors, frames, sidelites, anchors, hardware, finish, options and accessories.

Samples: Submit manufacturer’s samples of aluminum finish.

Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification.

Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the complete door opening installation in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the entrance and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.

Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.

QUALITY ASSURANCE

Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.

Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum 3 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

Source Limitations for ICU/CCU Entrances:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.

PROJECT CONDITIONS

Field Measurements:  Verify actual dimensions of openings to receive ICU/CCU entrances by field measurements before fabrication and indicate on shop drawings.

COORDINATION

Coordinate sizes and locations of recesses in concrete floors for recessed tracks and thresholds if applicable. Concrete work is specified in Division 03.

WARRANTY

General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

Manufacturer’s Standard Limited Warranty:  Manual ICU/CCU doors shall be free of defects in material and workmanship for a period of two years from the date of manufacturer shipment.

PRODUCTS

MANUFACTURER

- Record-USA

- 4324 Phil Hargett Court

- Monroe, North Carolina, USA

- (800) 438-1937

- NOTE:  Revise the following substitution clause as required by project requirements.  Select either Item “B” or “C”

[Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

[Substitutions:  Not Permitted.]

INTENSIVE CARE UNIT/CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

ICU/CCU entrances including the following:

Sliding panels, sidelites and aluminum frame.

Entrance header, guide system and carrier assemblies.

- NOTE:  Select entrance configuration(s) as required for the project

Record DS10 ICU/CCU Sliding Door Package (Basis of Design):

[Single slide, full breakout, ICU/CCU door system.]

Operation:  Manually operated.

Configuration:  Single slide, two equal panel unit with one operable leaf and one sidelite.

Minimum Clear Door Opening Width:  [41-1/2 inches for 8’-0” unit width.]  [44-1/2 inches for 8’-6” unit width.]

Breakaway Capability:  Sliding leaf and sidelite.

Mounting:  Overhead header installed between jambs.

[Single slide, fixed sidelite, ICU/CCU door system.]

Operation:  Manually operated.

Configuration:  Single slide, two equal panel unit with one operable leaf and one fixed sidelite.

Minimum Clear Door Opening Width:  [41-1/2 inches for 8’-0” unit width.]  [44-1/2 inches for 8’-6” unit width.]

Breakaway Capability:  Sliding leaf only.

Mounting:  Overhead header installed between jambs.

[Single slide, surface mounted, ICU/CCU door system.]

Operation:  Manually operated.

Configuration:  Single slide unit without sidelite.

Minimum Clear Door Opening Width:  [41-1/2 inches for 8’-0” unit width.]  [44-1/2 inches for 8’-6” unit width.]

Breakaway Capability:  Sliding leaf.

Mounting:  Surface mounted header installed on face of wall.

[Bi-parting, full breakout, ICU/CCU door system.]

Operation:  Manually operated.

Configuration:  Bi-parting, four equal panel unit with two operable leaves and two sidelites.

Breakaway Capability:  Sliding leaves and sidelites.

Mounting:  Overhead header installed between jambs.

[Bi-parting, fixed sidelite, ICU/CCU door system.]

Operation:  Manually operated.

Configuration:  Bi-parting, four equal panel unit with two operable leaves and two fixed sidelites.

Breakaway Capability:  Sliding leaves only.

Mounting:  Overhead header installed between jambs.

[Bi-parting, surface mounted, ICU/CCU door system.]

Operation:  Manually operated.

Configuration:  Bi-parting, two equal panel unit with two operable leaves and no sidelites.

Breakaway Capability:  Sliding leaves only.

Mounting:  Surface mounted header installed on face of wall.

ENTRANCE COMPONENTS

Stile and Rail Sliding Panels and Sidelites:

Material:  Extruded Aluminum, Alloy 6063-T5 or 6063-T6.

Door panels shall have a minimum .125 inch (3.2 mm) structural wall thickness including adjoining perimeter frames where applicable.

Aluminum extrusions shall allow for a factory installed, slide-in type gasket.

Door construction shall be by means of an integrated corner clip with 3/8 inch diameter all-thread through bolt from each stile.

Face of door stiles shall be flush with adjacent rails and muntin.

Glass stops shall be .062 inch (15.8 mm) wall thickness and shall provide security function as a standard by means of a fixed non-removable exterior section with glazing to be performed from the interior only.  Horizontal glass stops for 1/4 inch (6 mm) glazing shall be sloped.

Vertical Stiles shall be [narrow stile 2-1/8 inch (54 mm).]  [medium stile 4 inch (102 mm).]

Bottom Rails shall be [4 inch (102 mm).]  [7 inch (178 mm).]  [10 inch (254 mm).]

[Intermediate Muntin shall be [1-3/4 inch (45 mm).]  [4 inch (102 mm).]

Gasketing:  Slide-in type, replaceable pile mohair seals.

Bottom rails shall be provided with a concealed adjustable sweep gasket.

Glass:  Glazing shall comply with ANSI Z97.1, thickness as indicated.

- NOTE:  Select glazing types as required for the project.  Add “Locations” to each of the following if multiple types and/or thickness glazing is required.

Glazing Sliding Panels and Sidelite Panels:  [1/4” (6 mm)] tempered glass, unless otherwise specified.  [Optional glazing: 5/8” (16 mm) insulated glass, 1” (25 mm) insulated glass, 1-1/4” (31 mm) insulated glass]

Glazing Installation:  Dry glazing; wet glazing not allowed.

See Division 8 Section “Glazing” for requirements and the manufacturer instructions.

[All Glazing furnished “by others”.]

- NOTE:  Consult Record for integral blind information – glazing by Record

- NOTE:  Consider a lower panel with opaque glazing when specifying integral blinds – delete if not required

[Lower Lite Glazing Sliding Panels and Sidelite Panels:  1” (25 mm) overall thickness frosted insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.]

Frosted Glazing:  Opaque, acid etched on #2 or #3 surface.

[Upper Lite] Glazing with Integral Blinds Sliding Panels and Sidelite Panels:  1-1/4” (31 mm) overall thickness insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.]

Integral Blinds:  Glass to have blinds installed between glass lites.

Blinds to be mechanically gear-driven tilt micro-blind installed in the sealed insulating glass unit.  Internally mounted control assembly that is coupled to the external operator controls the tilting of blind slats.

Tilt Operator:  Thumb wheel, dual control.

Glazing Installation:  Dry glazing; wet glazing not allowed.

See Division 8 Section “Glazing” for requirements and the manufacturer instructions.

Door Carriers:  Manufacturer’s standard carrier assembly that allows vertical adjustment.

Sliding Panel Door Carriers:

        - Roller Wheels:  Two heavy duty Delrin roller wheels per wheel assembly, for a total of four (4) roller wheels, 1-7/16 inch (36.51 mm) diameter, per active door leaf for operation over a replaceable aluminum track. Single journal with sealed oil impregnated bearings.

        - Two (2) heavy duty self-aligning anti-risers per leaf.

Framing Members:  Provide ICU/CCU entrances as complete assemblies.  Manufacturer’s standard extruded aluminum framing reinforced as required to support loads.

Vertical Jambs:  [1-3/4 inches (44.5 mm)]  [1 inch (25.4 mm)]  by 4-1/2 inches (114.3 mm).

Header:  Extruded aluminum header with a replaceable aluminum track, mounted between the jambs and extending full width of entrance.  Header to conceal door operators, carrier assemblies, and roller track; complete with hinged access panel for service and adjustment.

Header Capacity:  Capable of supporting active breakout leafs up to maximum of 220 lb (100 kg) per leaf.

- NOTE:  All headers are to be anchored to overhead framing per manufacturer’s recommendations.

- NOTE:  The framing surrounding the opening needs to be capable of supporting no less than 440lbs for single slide, 880lbs for bipart or single slide telescopic. This is a double the weight of the door panel safety factor.

Header Size:  4-1/2 inches (114.3 mm) wide by 4-1/2 inches (114.3 mm) high.

Gasketing:  Slide-in type, replaceable pile mohair seals.

Header Access:  Continuous hinge at top of header allows cover to swing and allow complete access to operator and internal electronic and mechanical assemblies.

- NOTE:  Entrance needs to be connected to the building ground for the following option – work by others

[Anti-Static Grounding:  Fabricate ICU/CCU entrances to be internally grounded to reduce static shock.]

HARDWARE

Provide manufacturer’s standard hardware as required for operation indicated.

Breakaway arms and bottom pivot assembly shall allow panels to breakout to 90 degrees.  Force to breakout sliding panel adjustable to maximum 50 lbf (222 N).

Nurse Assist magnetic catch(s) to retain breakout door and sidelite panels in the closed position.

[Gas regulated damper to control movement of breakout panels.]

- NOTE:  Optional positive latching for sliding ICU/CCU door system

[Latching hardware shall be provided as indicated.]

[Positive Latch: Mortise type self-latching hookbolt, BHMA A156.5, Grade 1, with lever handles on each side.]

[Lever Style:  End of lever to have a return towards door face.]

Manual operated flush bolt to secure sidelite panel(s) that breakout.

- NOTE:  Recessed pull/C-shaped  pull are provided standard on sliding ICU/CCU doors, not available with positive latching door hardware

[Door pulls shall be provided as indicated.]

[Manufacturer’s recessed pull installed on breakout side and surface-mounted, 10” C-shaped door pull installed on non-breakout side of active door leaves.  Door pull mounting shall not decrease clear opening width.]

- NOTE:  Optional C-shaped pull on both sides of sliding ICU/CCU door system

[Manufacturer’s surface-mounted, 10” C-shaped door pull installed on both sides of active door leaves.  Door pull mounting shall not decrease clear opening width.]

- NOTE:  Optional self-closing device for manually operated sliding ICU/CCU doors

[Self-closing device shall be provided where indicated.]

A non-electrified, adjustable speed, rack and pinion mechanism, which will close door to a positive latched position.

- NOTE:  Optional magnetic hold-open device for ICU/CCU sliding entrances

[Magnetic hold-open devices tied into the building fire alarm/sprinkler system, which will upon receiving a signal, release the self closing sliding door leaf.]

Magnetic device to accept 12-24vdc with no more current draw than 120mA with a hold force not to exceed 30lbs for manual door release.

Guide Track/Threshold:  Manufacturer’s threshold as indicated.

- NOTE:  Option “a” is the manufacturer’s standard threshold/track for sliding ICU/CCU entrances and Option “b” is optional – full breakout entrance

[Full Breakout Trackless Design:  Floor mounted guide track and threshold not allowed.]

Breakout from a full open position only.

[Full Breakout Entrance Guide Track:  Floor mounted aluminum guide track(s) adjacent to the sidelite portion of the sliding ICU/CCU entrance.]

[Surface mounted track.]  [Recessed mounted track.]

Guide track shall allow breakout from any position except when door is latched.

- NOTE:  Option “c” is the manufacturer’s standard threshold/track for sliding ICU/CCU entrances - fixed sidelite entrance

[Fixed Sidelite Entrance Guide Track:  Aluminum guide track integrated in the bottom of the sidelite portion of the sliding ICU/CCU entrance.]

Guide shall allow breakout from any position except when door is latched.

- NOTE:  Option “d” is the manufacturer’s standard - surface mounted entrance

[Surface Mounted Entrance Guide Track:  Aluminum fixed sidelite guide track mounted along the face of the wall.  The track shall not extend past the jamb into the door opening.]

Guide track shall allow breakout from any position except when door is latched.

ALUMINUM FINISHES

Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

[Anodized Finish:]

[AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

[AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

[AAMA 611, Custom anodized to match architect’s sample.]

[Painted Finish:]

[Powder coat painted to match architect’s sample.]

[Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

[To match architects sample.]

- NOTE:  Delete following if MicroShield is not required.  Consult Record for availability of MicroShield with anodized and painted aluminum finishes

[MicroShieldTM antimicrobial silver-based ion, baked-on enamel finish on all exposed surfaces including door pulls, door extrusions, rails and header.]

Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew by the controlled release of silver ions that attack microbes and inhibit the growth on the treated surfaces.

Coating to be EPA registered resulting in a safe and non-toxic finish; chlorinated or synthetic chemical finishes will not be accepted.

EXECUTION

EXAMINATION

Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance.

Proceed only after such discrepancies or conflicts have been resolved.

INSTALLATION

Do not install damaged components.  Fit frame joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

Install intensive care unit/critical care unit (ICU/CCU) entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

Install surface mounted hardware using concealed fasteners to greatest extent possible.

Set headers, carrier assemblies, tracks, operating brackets and guides level and true to location with anchorage for permanent support.

Where aluminum will contact dissimilar metals, concrete, or masonry, protect against galvanic action and corrosion.

- NOTE:  Retain the following if magnetic hold-open devices are required

[Magnetic Hold-Open Devices:  Connect magnetic hold-open devices to the building fire alarm/sprinkler system as specified in Division 26 and Division 28 Sections.]

Holding force not to exceed 30lbs for manual door release.

Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to provide a weather tight installation.

Set thresholds, bottom guide and track systems and framing members in full bed of sealant.

Seal perimeter of framing members with sealant.

ADJUSTING

Adjust alignment of entrances and hardware for smooth, safe operation with minimum air infiltration.

Verify installation and alignment of all entrance gasketing as required for minimum air infiltration and compliance with specified standards.

CLEANING AND PROTECTION

Clean adjacent surfaces soiled by door installation.

Clean glass and metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages to match original finish.

DEMONSTRATION

Engage a factory-authorized representative to train Owner's maintenance personnel to adjust, operate, and maintain safe operation of the door.

END OF SECTION