SECTION 11 14 00 – PEDESTRIAN EXIT LANE BREACH CONTROLS

GENERAL

- <SPECIFIER:  Edit this specification as required for the project>

SECTION INCLUDES

This section covers the furnishing and installation of a complete Automatic Security Breach Control System.  Provide a complete system that has been fabricated and tested for proper operation at the factory.  System includes sidewalls, canopy, ceiling, automatic doors, hardware, glass, drive systems, sensor systems and guide rails.

RELATED SECTIONS

07 90 00 – Joint Protection

08 40 00 – Entrances, Storefronts, and Curtain Walls

08 71 00 – Door Hardware

08 80 00 – Glazing

09 60 00 – Flooring

26 00 00 – Electrical

QUALITY ASSURANCE

Manufacturer shall be a company specializing in the supply of automatic security breach doors with a minimum of 10 years’ experience.

Manufacturer must be able to provide a minimum of 10 references and have a minimum of 30 exit lane breach control systems installed and operating in North American airports.

Manufacturer must have received TSA approval for unmanned operation at all installations.

SUBMITTALS

Product Data: Provide complete product and installation documentation as provided by the manufacturer.

Shop Drawings: Provide shop drawings including elevations, sections, and details of entrance construction.  Include profiles, dimensioned layout, operator, motion /presence sensor control devices, indicating assembly, finish, glazing, electrical, and anchoring requirements.

Provide manufacturer’s operating and maintenance manual.  The manual to include the name, address, and contact information of the manufacturer providing the entrance and their nearest service representatives.  A spare parts list shall also be included.

Provide manufacturer’s warranty documentation.

DELIVERY, STORAGE, AND HANDLING

Deliver materials to job site in manufacturer’s packaging, undamaged complete with installation instructions.

Store off ground, under cover, protected from weather and construction activities.

FIELD CONDITIONS

Install security breach doors on finished floor only.  Floor must be level +/- 1/16” (1.5mm) at all locations within the footprint of the security breach door.

Shop drawings must be reviewed and confirmed by the General Contractor.  Verify actual dimensions of openings to receive automatic entrances by field measurements before fabrication and indicate on shop drawings.

Coordinate power requirements, layout, and connections to power supplies with installation of security breach door.

WARRANTY

Project Warranty:  Security breach door system shall be warranted against defect in material and workmanship for a period of one year from the date of substantial completion or one and one-half years from the date of manufacturer shipment.  This warranty excludes glass breakage, normal wear on finishes, or damage that occurs due to abuse, misuse or acts of God.

During the warranty period a factory-trained technician shall perform service and repairs. An inspection shall be performed after each adjustment or repair.

During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.

SERVICE

Manufacturer to provide a per lane cost to provide once or twice a year on site service by factory employed and trained technicians.

MANUFACTURING LOCALE

The security exit lane shall be wholly manufactured in the USA and using metals acquired in the USA.  Assembly of electronics, components, and structure shall take place fully in a manufacturing facility in the USA.

PRODUCT

MANUFACTURER

- Record-USA

- Monroe, North Carolina, USA

- (800) 438-1937

AUTOMATIC SECURITY BREACH CONTROL SYSTEM

The FlipFlow security breach door system is an automatic high-capacity anti-pass back system, providing the regulations of passenger/user traffic flow in airports, industrial manufacturing facilities, and other sensitive areas in various types of buildings. Pedestrians may pass through the FlipFlow in single file and in one direction only. Attempts at reverse entry are detected by an intelligent sensor system and the automatic doors will inhibit such action. In addition, an alarm is generated locally, and an alert message is generated for remote monitoring.

APPLICATIONS

Passenger flow regulation in airports (separates the secure airside from the non-secure landside)

Protection of other sensitive areas in seaports and railway stations.

Access to sensitive areas in public, commercial, and industrial buildings

Entrance to court houses or judicial buildings

Side entrance in supermarkets

CONSTRUCTION

Self-supporting aluminum construction, clad in stainless steel. The unit is capable of free-standing, however, units installed in seismic areas requiring special anchoring and attachment shall be tied into a supporting structure.

Triple (three sets of doors) and twin (two sets of doors) configurations.

Double leaf Record door operators are provided as standard for a long life.

Doors are supplied with robust electromechanical brakes or optionally electromagnetic locks to inhibit door open motion in fully closed position.

A master control, supplemented with a modular, expandable sensor system, monitors passenger flow.

Transparent side panels in laminated security glass facilitate monitoring requirements.

Passage status is indicated by red/green traffic-light style indicators at both the entrance and exit doors.

Interior lighting is provided by six (6) LED spotlights.

Three widths area available

900mm (35’’ Clear Opening) opening width to allow for wheelchair access

1100mm (43” Clear Opening) opening width to allow for wheelchair access

1200mm (47” Clear Opening) opening width to allow for wheelchair access

- <SPECIFIER:  Select either Twin or Triple configuration>

[Configuration:  Triple.]

Triple (3 doors) 6345mm (20’9-3/4”) long x 2363mm (7’-9”) high

Extension (optional) 1956mm (6’-5”) long x 1042mm (3’-5”) high

[Configuration:  Twin.]

Twin (2 doors) 3248mm (10’-7 ¾”) long x 2363mm (7’-9”) high.

Extension (optional) 1956mm (6’-5”) long x 1042mm (3’-5”) high

If installed utilizing existing transom, location for structural means shall be determined by facility.

The space between the top of the unit and the ceiling above must be closed off, or limited, to prevent objects from being thrown over, or set on top of the unit.

Object detection on all sidewalls, ceiling and floor is required

Flow mode to interlock mode must have an optional automated setting and able to be controlled without personnel having to physically visit the lane.

Wall structures and posts shall be clad in stainless steel, unless otherwise directed, allowing for easy removal of the clad covers for maintenance and replacement of damaged components in the form of dents, scratches, etc., from luggage and regular use.

Units must be enclosed with hard ceiling (no open top units).

SENSORS

Sensors for the SEL must utilize TOF-3D, an automatic anti-return detection sensor with high resolution. The TOF 3-D sensor utilizes a matrix of 500 pixels with which the sensor measures the distance to the object and captures it three-dimensionally. This is made possible by Time-Of-Flight (TOF) technology which calculates the distance to the object by measuring the light travel time.

This sensor shall also facilitate reliable anti-return object detection under adverse environmental influences such as extraneous light, humidity, or dirt. This makes it possible to determine the presence, stature and movement of people and objects within the field of vision with very high accuracy.

The sensor system shall not require dependency from low or ambient light and also perform in complete darkness in case of power outages or emergency scenarios. Detection of small objects and crawling people within the tunnel while the doors are open is mandatory. Alternates will not be accepted.

Video analytic systems not permissible.

GLAZING

Wall panels and glass doors are 5/16” laminated safety glazing.

Extensions are ½” safety glazing.

OPERATION MODES

FLOW MODE

Motion sensor detects approaching pedestrian(s) and actuates entrance doors.

Pedestrian(s) proceed into the anti-pass-back passageway.

The entrance doors close when motion is no longer detected and a presence is not detected in the door leaf swing areas.

The pedestrian(s) continue through the passageway.

A motion sensor in the passageway detects pedestrian(s) and actuates the exit doors. If equipped with three doors the process is repeated through a second set of doors and into a second chamber, at which time the exit doors are actuated.

Infra-red cameras are used to body track heat signature direction and detect possible pass-through attempts

Pedestrian(s) exit the anti-pass-back passageway(s).

Red/Green traffic lights indicate when passage is allowed.

Interior spotlights are on.

Both entrance middle (if equipped) and the exit doors may be open at the same time.

Pedestrians who passed more than halfway through the passageway cannot reverse direction without causing the entrance doors to close and lock.

INTERLOCK MODE

Motion Sensor detects approaching pedestrian(s) and actuates entrance doors.

Pedestrian(s) proceed into the anti-pass-back passageway.

Threshold safety beams:

Inhibit closing if the threshold is occupied.

After the entrance doors have closed, the interior doors (if equipped) and exit doors will automatically open, allowing exit from the passageway.  A pedestrian in the passageway will have a nominal 5-6 second delay before exiting.

The entrance door closes when motion is no longer detected, or if three or more pedestrians have entered the passageway.

When all pedestrians have exited the passageway, the interior doors (if equipped) and exit doors will close.

The interior of the passageway(s) are scanned for objects, and if clear, the entrance doors will automatically reopen.

If objects are detected, the entrance doors will remain closed and the interior doors (if equipped) and exit doors will reopen and remain open until the object has been removed.

Red/Green traffic lights indicated when passage is allowable.

Interior spotlights are on.

The entrance, interior doors (if equipped) and the exit doors are interlocked and prevented from being open at the same time.

OPEN MODE

Entrance and exit doors are kept open.

Back flow detection can be disabled to allow free passage in both directions of the tunnel.

The monitoring sensor systems are disabled (optional alarm contact available to indicate incorrect walking direction).

Green traffic light indicates unhindered passage.

Interior spotlights are on.

LOCKED MODE

Both entrance and exit doors closed and locked.

Traffic through the FlipFlow is inhibited in both directions.

Red traffic lights indicate no access.

Interior spotlights are off.

EMERGENCY MODE

Both automatic doors are equipped with battery backs.

During a power failure, the doors complete a final movement (entrance doors are closed and locked; exit doors are opened).  The tunnel can be feely exited to the landside.

An emergency open button as well as a phone inside the tunnels is a recommended option for emergency evacuations.

EVACUATION MODE

Allows the opening of both doors in emergency evacuation scenarios under the highest priority without addressing any means of security.  This mode will be triggered via a hardwired contact or via a TCP/IP connection remotely.  See also section 2.10.

MAINTENANCE AND CLEANING

An optional key switch (by others) can be installed to allow maintenance personal to access the lane during a preset time.  During this time, the alarms are not triggered.

Allows a service technician to access, service, adjust and test the FlipFlow.

A local audible alarm is actuated if the maintenance switch is not reset after a preset, configurable time delay.

Dry contact output can be used for remote monitoring of the service hatch access.

An optional contact for key switch (by others) that allows for simple cleaning of the passageway is available.

Access to interior of passageway is by opening the exit doors; the entry doors are closed and locked.

Alarm outputs are suppressed.

A local audible alarm is actuated if the cleaning mode switch is not reset after a preset, configurable time delay.

Dry contact output, similar to the above alarm outputs, can be used for remote monitoring of service hatch access.

AUTOMATED FLOW TO INTERLOCK MODE

Detects flow increases and decreases and automatically converts Flow Mode to Interlock Mode and vice versa without the requirement of airport personnel having to physically go to the lane.

OPTIONS

INSIDE MONITORING AND OBJECT DETECTION

Infrared and microwave sensors allow for monitoring the interior passageway of the FlipFlow.

Detection of objects as small as 2” x 2” x 2” (50mm x 50mm x 50mm) at the floor and ceiling and sidewalls.

OBJECT DETECTION

The following options are available individually or in combination:

Detection of stationary objects attached to interior ceiling, sidewalls, and floor.

SIDE RAILS AND BARRIER AT EXIT

Additional glass guide rails are installed on the exterior or the exit doors, and:

Include two low height stainless steel swing barrier gates.  This will increase security and deter attempts to enter the exit door from the landside.  Inhibiting access on the landside will reduce nuisance interference of the exit doors and subsequently increase throughput of the FlipFlow.

INTEGRATION OR ACCESS CONTROL SYSTEM

A special operation mode is available in the closed/locked position:

The connection of an access control system (card reader, etc.) admits a single passage of the FlipFlow from the landside to the airside.

For security reasons, only door is opened at the same time.

After the passage has completed, the designated operation mode is resumed.

SERVICE DISPLAY

The Record service display module is designed primarily for use by service technicians, and provides the following features:

Adjustments and modification of operational mode parameters.

Adjustment of various timers according to customer’s requirements.

Display status of digital inputs and relay outputs.

Display error messages in user-friendly text.

Password protected access levels.

To meet individual requirements, this useful tool is provided in two alternative physical packages:

Securely integrated into each FlipFlow, or

As a portable service tool, compatible with all current FlipFlow units.

BATTERY BACK UP

One cycle open after detection of loss of power.

Implementation of an UPS (uninterrupted power supply) backup system to guarantee the operation of up to three hours.

REAL TIME MONITORING

Offers airport security personnel the ability to monitor the status of all FlipFlow units.

When an airport allows temporary access to the local PC that runs the Record REALTIME software via remote monitoring, Record has the ability to support and assist in resolving problematic occurrences.

Allows for security personnel to receive email alerts of events.

Allow for staff to monitor doors with smart phone or tablet type of devices.

INCORRECT USE AND ALARM OUTPUTS

A local audible alarm is actuated when an alarm occurs.  A PLC output, rated 25W at 24VDC, will actuate, and can be used to turn on a flashing strobe for visual notification.  Additionally, the following individual alarm outputs are provided, each with dedicated dry contacts, and can be used for remote monitoring and/or integration with a building management system.

Intrusion:  An audible alarm is immediately enabled when the pass-back sensors are triggered while the entry door was still open signaling the possibility that a person was able to clear the doors prior to closing and locking.

Wrong Direction:  An audible alarm is immediately enabled if a pedestrian has traveled more than half-way through the passageway, stops, and attempts to turn around and walk back through the entry doors.

Flow Disturbance:  An audible alarm is enabled when normal traffic flow has been hindered by external influences.  This includes obstructing access to traveling through the FlipFlow, and/or detection of a person or object in the FlipFlow passageway when both entry and exit doors are closed.

Technical Disturbance:  A malfunction in either of the door operators or the monitored sensors and cameras will enable the audible alarm and actuate a separate dry contact.

8 dry contact outputs are available

REMOTE CONTROL

Remote Control: Inputs are provided for external control of the following functions and can be controlled by remote contacts of a building management system and have priority of the local controller.

Immediately open both entry, interior doors (if equipped), and the exit doors. (Evacuation Mode)

Immediately close and lock the entry doors and open the interior doors (if equipped) and the exit doors.

Switch the FlipFlow from interlock mode and back automatically.

ELECTRICAL/CAT6

The security exit breach lane shall consume no more than 1000W of electricity at full load power for Flip Flow Triple with extension gates.  200W in standby mode.

Power:  120 VAC, 1 phase, 20 amp dedicated circuit per lane shall be provided by others.

CAT6:  Required ethernet connection shall be provided by others.

ALUMINUM FINISHES

Comply with NAAMM’s “Metal Finishes Manual for Architectural and Metal Products” for applying and designing finishes. Finish designations beginning with “AA” comply with requirements established by American Architectural Manufacturers Association (AAMA).

- <SPECIFIER:  Select finish as required for project>

[Kynar Paint Coating:  As selected by Architect from full range of industry colors and color densities.]

[Powder Coat:  To match Architect’s sample.]

[Stainless Steel Clad:  [Polished, non-directional finish.]  [Satin finish.]

[Brass Clad:  [Polished, non-directional finish.]  [Satin finish.]

EXECUTION

INSPECTION

Installers shall examine the locations and advise of any site conditions that are unacceptable for the proper installation of the product.  These conditions include, but are not limited to the following:

Identification and planning for expansion joints, project access, onsite staging areas.

Site configuration/temporary construction enclosures, and work hours as related to other activities.

Floor must be leveled and smooth with no deviations in excess of 1/16” from 12 foot location, in any direction.

The ability for the breach door system to be installed level shall be verified prior to installation of any part of the security breach door system.

Power supply must be installed and verified to be of the correct voltage.

Required facility systems such as security interface and electrical power must be ready for connection/termination at the time of installation.

INSTALLATION

System shall be installed by factory employed and certified installers.

System shall be commissioned by factory technicians.

System shall be installed with manufacturer’s provided instructions.

System must be set level, plumb, with uniform hairline joints, and anchored security into place.

Assembly dimensional tolerances, as indicated within manufacturing recommended instructions must be maintained.

All alignment with adjacent work must be maintained.

Coordinate installation with facility requirements such as electric power, security interface and Cat 6 connections.

Door(s) must meet all safety codes and standards.

Adjust door, hardware and sensors for smooth operation and smooth performance.

Installation crew should be proven to have five confirmed and successful installations within the United States.

Factory installer shall demonstrate to the owner’s dedicated staff the proper operation of the exit lane system and the necessary service requirements such as lubrication, cleaning, and inspection of components.

ADJUSTING

Operational adjustments in the field shall be achievable with trained field personnel.  An engineer from the manufacturer should not be required to adjust the physical system or software programming.

CLEANING

Clean glass and metal surfaces promptly after installation.  Remove excess glazing and sealant compounds, dirt, and other substances.  Repair damaged finish to match original finish.

Clean adjacent surfaces soiled by installation.

DEMONSTRATION

Manufacturer/installer shall provide two hours of on-site training for the necessary airport personnel on the functions and use of the exit lanes.

MAINTENANCE PLAN

Manufacturer shall offer an onsite annual, semi-annual, or quarterly maintenance plan options at an additional cost for planned service provided by factory trained technicians to suit the owner’s needs.

- END OF SECTION 11 14 00