SECTION 08 71 13 – AUTOMATIC DOOR OPERATORS

GENERAL

SUMMARY

- <SPECIFIER:  Edit this specification as required for the project>

- <SPECIFIER:  This specification is for automatic door operators complying with ANSI/BHMA A156.19 for power assist and low energy door applications.>

This section includes the following types of automatic door operators:

In-ground, low energy door operators for swinging doors.

Related Sections:

Division 7 Sections for caulking to the extent not specified in this section.

[Division 8 Section “Aluminum-Framed Entrances and Storefronts” for entrances furnished separately in Division 8 Section.]

[Division 8 Section “All-Glass Entrances and Storefronts” for entrances furnished separately in Division 8 Section.]

[Division 8 Section “Door Hardware” for hardware to the extent not specified in this Section.]

Division 26 and 28 Sections for electrical connections including conduit, liquid- tight connections, and wiring for automatic entrance door operators and access control devices.

REFERENCES

References:  Refer to the version year adopted by the Authority Having Jurisdiction.

ANSI A117.1 - Accessible and Usable Buildings and Facilities.

ICC/IBC - International Building Code.

NFPA 70 - National Electrical Code.

NFPA 101 - Life Safety Code.

NFPA 105 - Installation of Smoke Door Assemblies.

American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA).

ANSI/BHMA A156.19 Standards for Power Assist and Low Energy Power Operated Doors.

American Association of Automatic Door Manufacturers (AAADM).

International Electrotechnical Commission (IEC) Ingress Protection (IP).

IEC 60529 Degrees of Protection Provided by Enclosures.

International Code Council (ICC).

[IBC:  International Building Code.]

[CBC: California Building Code.]

DEFINITIONS

Activation Device: Device that, when actuated, sends an electrical signal to the door operator to activate the operation of the door.

Knowing act:	Consciously initiating the opening of a power operated door using acceptable methods including wall mounted switches such as push plates and controlled access devices such as keypads, card readers and key switches.

Safety Device: A device that detects the presence of an object or person within a zone where contact could occur and provides a signal to stop the movement of the door.

Double Egress Doors:  A pair of doors that swing with the two doors moving in opposite directions and no mullion between them.

PERFORMANCE REQUIREMENTS

Automatic door equipment accommodates medium to heavy pedestrian traffic.

Ingress Protection (IP) against environmental conditions:

IP69 – Completely protected against dust; capable of withstanding prolonged periods of immersion in water; and capable of withstanding high-pressure, high-temperature jet sprays, steam-cleaning, or washdowns.

Opening Force Requirements:  Doors shall open with a manual force, not to exceed 30lbf (133N) to set the door in motion and 15 lbf to fully open the door applied at 1” (25 mm) from the latch edge of the door.  The force required to prevent a stopped door from opening or closing shall not exceed 15 lbf (67 N) measured 1” (25 mm) from the latch edge of the door at any point during opening or closing.

Closing Time:

Doors shall be field adjustable to close from 90 degrees to 10 degrees in 3 seconds or longer as applicable per ANSI/BHMA A156.19 standards.

Doors shall be field adjusted to close from 10 degrees to fully closed in not less than 1.5 seconds.

SUBMITTALS

Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.

Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, operator, motion /presence sensor control device, anchors, hardware, finish, options and accessories.

Indicate required clearances, and location and size of each field connection.

Indicate locations and elevations of entrances showing activation and safety devices.

Wiring Diagrams:  For power, signal, and activation / safety device wiring.

Manufacturers Field Reports:  Submit manufacturer’s field reports from AAADM certified technician of inspection and approval of doors for compliance with ANSI/BHMA after completion of installation.

Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the work of this section in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the operators and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.

Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.

QUALITY ASSURANCE

Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.  Manufacturer to have a company certificate issued by AAADM.

Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum 3 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

Certified Inspector Qualifications: Certified by AAADM.

Source Limitations for Automatic Door Operators:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.

Operator shall be furnished complete with the cement case, floor plate, drive mechanism, arm, and spindle from a single manufacturer.

Certifications: Operators shall be certified by the manufacturer to meet performance design criteria in accordance with the following standards.

ANSI/BHMA A156.19 American National Standard for Power Assist and Low Energy Operated Doors.

NFPA 101 - Life Safety Code.

Emergency Exit Door Requirements: Comply with requirements of authorities having jurisdiction for automatic entrance doors serving as a required means of egress.

COORDINATION

Coordinate door operators with doors, frames and related work to ensure proper size, thickness, hand, function and finish. Coordinate hardware for automatic entrances with hardware required for rest of the project.

Coordinate sizes and locations of recesses in concrete if applicable. Concrete, reinforcement and formwork are specified in Division 03.

Electrical System Roughing-in: Coordinate layout and installation of power door operators with connections to power supplies and access control system as applicable.

WARRANTY

General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

Automatic Door Operators shall be free of defects in material and workmanship for a period of one year from the date of manufacturer shipment.

During the warranty period a factory-trained technician shall perform service and affect repairs. An inspection shall be performed after each adjustment or repair.

During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.

PRODUCTS

MANUFACTURER

Manufacturer:  Record-USA, 4324 Phil Hargett Ct., Monroe, NC 28110.  (800) 438-1937

- <SPECIFIER:  Revise the following substitution clause as required by project requirements.  Select either Item “B” or “C”>

[Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

[Substitutions:  Not Permitted.]

SWING DOOR OPERATORS

Model:  Record C127X in-ground, low energy automatic door operator:

Reference Standard:  ANSI/BHMA A156.19.

Configuration:  Operator to control single swinging doors and pairs of swinging doors as indicated on the drawings and specified below:

Traffic Pattern:  [One way.]  [Two way.]

[Pairs of Doors:  [Simultaneous swing.]  [Single leaf operation.]

[Double Egress:  [Simultaneous swing.]  [Independent operation.]

Automatic Door Operator:  Electro-mechanical, non-handed operator, powered by 24 volt, 1/4 hp pulse-modulated motor.

Automatic operator shall be capable of operating and controlling up to a 1323 pound (600 kg) door.

In-Ground Operator Enclosure and Drive Unit:

Fully tested IP rating 67, 68, and 69 with certificate.

Cement case shall be stainless steel, fully welded enclosure.

All in One Design – No external control cabinet required.

External Opening Angle adjustment required.  Adjusting door opening angle should not require the operator seal to be removed.

Removable top case cover shall be die-cast aluminum.

Cover shall be sealed to drive unit housing by a neoprene gasket.

Drive Mechanism Assembly:  Manufacturer’s drive mechanism assembly designed to provide swing door operation from an in-ground automatic door operator in either a center drive or offset drive configuration.

- <SPECIFIER:  Select either option “a” or “b” below.  Center drive and offset drive do not reflect the hanging method of the door, rather it reflects the location of the drive axis in relationship to the centerline of the housing.  Center drive and offset drive variations allow for multiple installation options.  Offset drive may be utilized on exterior applications to position the drive unit completely inside of the building.>

[Center Drive]

[Offset Drive]

Connecting hardware to door shall be a door arm attached to the bottom rail of the swing door.  Top pivot assembly or hinges shall be supplied by Division 8 Section “Door Hardware”.

- <SPECIFIER:  Verify hanging method and door arm required for the project.  Select either option “a” or “b” below.  Option “a” is typically used with center hung pivot doors and can support the weight of the door.  Option “b” is typically used at doors that are hung using butt hinges, continuous hinges, or offset pivots and the door weight is supported by the hanging hardware.  Consult Record if option “b” is selected.>

[Operator shaft shall be directly coupled to lever arm assembly. (Direct Drive Option)]

[Operator shaft shall be coupled to sliding arm assembly.  Weight of the door shall be fully supported independently.  Door weight shall not be supported by the operator or the gearbox assembly.  (Independent Drive Option)]

Operator Temperature Range:  Capable of operating within temperature ranges of -40 F to 140 F (-40 C to 60 C).

Electrical Characteristics:  Maximum power consumption is 200 watts (1.67 amps at 120 VAC), 50/60hz, built-in thermal overload protection.

Electronic Controls: CanBus based microprocessor controlled unit shall control the operation and switching of the swing operator. The microprocessor control to provide low voltage power supply for all means of actuation.  The controls include time delay for normal cycle.

Control will accept signals from peripheral devices such as motion and safety sensors.

On board system monitoring with 24/7 feedback with the S.M.A.R.T. Panel LCD Display. The unit will display the status of the operator, any faults that occurred and contact information for fault notification.

Microprocessor shall be easily updated with new software versions.

Door Operation:

Power Open: When an opening signal is received, the door will open at the pre-set operator opening speed. At back check, the door slows, and at the pre-selected opening angle the door stops.

If the door is obstructed while opening, it will either stop or reverse (field selectable).

The open position is held by the motor.

Opening Angle: The operator shall have a field adjustable opening angle from 70 degrees to 120 degrees.

Spring Close: An adjustable tension spring shall provide closing.

When the hold open time has elapsed, the operator will close the door automatically, using the motor and spring force. The door will slow at latch check.

The door is kept closed by spring power or extended closing force by the motor.

Power Assist: Operator can be adjusted to provide a lower opening force while pushing or pulling the door manually.  Operator allows the door to close when an opening force is no longer applied to the door.

Power assist force is field adjustable from 5 lbf to 15 lbf maximum.

Stack Pressure Control: Multiple electronic options shall be selectable in the software.

Door Coordinator: Door movement for a pair of doors with an astragal is sequenced to allow for coordinated opening and closing of doors.

Cycle Counter:  Operator has integrated digital cycle counter that includes total operation time.

SIGNAGE: Provide signage in accordance with ANSI/BHMA A156.19.

[ACTIVATION BY SMOKE EVACUATION SYSTEM]

- <SPECIFIER:  Delete this entire option if not required – Review operation with Architect>

[General:  Provide activation by the smoke evacuation system and/or fire detection system.  Coordinate other required activation devices and safety devices with door operation and door operator mechanisms.]

[Activation:	Smoke evacuation system and/or fire detection system shall provide activation of the operator by means of a normally open maintained contact to control the opening and closing of the door systems in the event of an alarm condition.  Doors are to be held open until the smoke evacuation/fire detection system is reset.]

ACTIVATION DEVICES

- <SPECIFIER:  Select the type of activation devices and safety devices required for the project>

General:  Provide activation devices in accordance with ANSI/BHMA standards, for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate activation and safety devices with door operation and door operator mechanisms.

- <SPECIFIER:  Select the type of knowing act activation devices if required for the project>

[Knowing Act Activation Device:]

[Push Plate:  Hard wired, [4-1/2 inch square]  [6 inch round] stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

[Push Plate:  Jamb mounted, hard wired, 1-1/2 inch x 4-3/4 inch, stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

[Push Plate:  Radio controlled, wireless, [4-1/2 inch square]  [6 inch round]   stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

[Sensor Plate:  Touchless, [2-3/4 inch x 4-1/2 inch]  [4-1/2 inch square] activation senor plates, black polycarbonate with white letters.  Microwave technology has an adjustable range of 2 inches to 24 inches.]

- <SPECIFIER:  Manual door operation is a standard feature of the door operator>

Manual Operation:

[Operator shall allow manual door operation with operational forces adjustable from 5 lbf to 15 lbf maximum.]

- <SPECIFIER:  Delete the above when specifing the power assist option>

- <SPECIFIER:  Specify the power assist option where manual operation is desired without “knowing act” activation including large and/or heavy doors requiring manual operation>

[Operator shall provide power assist function to the doors to provide ease of manual operational forces.]

Manual push force shall be adjustable from 5 lbf to 15 lbf maximum.

- <SPECIFIER:  Consult Record for “push and go” operation option>

[Operator shall provide “push and go” operation allowing door to open automatically after activation by manually pulling or pushing on the door.]

- <SPECIFIER:  Consult Record for safety device recommendations – safety sensors are not required by ANSI/BHMA A156.19 for low energy operators>

FLOOR PLATE

Floor Plate:  Manufacturer’s standard floor plate as indicated.

[Stainless steel floor plate.]

- <SPECIFIER:  Select either Option 1 above or Option 2 below>

[Terrazzo cover pan.]

EXECUTION

EXAMINATION

Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance of swinging power operated doors.

Examine roughing-in for electrical source power to verify actual locations of wiring connections.

Verify that all electrical penetrations into the cement case enclosure have liquid tight fittings.

Water-test electrical conduit penetrations (high volt and low volt connections) in cement case to assure leak-free system.

Proceed only after such discrepancies or conflicts have been resolved.

INSTALLATION

Do not install damaged components.  Fit joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

Operators:  Install automatic door operators plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

Install in-ground operator housing in accordance with manufacturer’s instructions and reviewed shop drawings.

Install operator drive mechanism assembly in accordance with manufacturer’s instructions.

Adjust operator and drive mechanism to achieve smooth operation including back-check, latch, and proper limit stops.

Install exposed to view fittings using concealed fasteners where possible.

Install threshold and operator fittings per manufacturer’s instructions.

Door Operators:  Connect door operators to electrical power distribution system [including smoke evacuation system and/or fire detection system] as specified in Division 26 Sections.

Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to seal between the operator housing and the adjacent surfaces and provide a water-tight closure.

Signage:  Apply signage on both sides of each door and sidelite as required by ANSI/BHMA A156.19 and manufacturers installation instructions.

ADJUSTING

Adjust automatic door operators, controls and hardware for smooth and safe operation and for weather tight closure. Adjust doors in compliance with ANSI/BHMA A156.19.

FIELD QUALITY CONTROL

Before placing doors into operation, AAADM certified technician shall inspect and approve doors for compliance with ANSI/BHMA A156.19.  Certified technician shall be approved by manufacturer.

CLEANING AND PROTECTION

Clean adjacent surfaces soiled by automatic door operator installation.

Clean metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages and finish to match original finish.

END OF SECTION